1.0	SCOPE

1.1	Purpose

This document defines the requirements and responsibilities for design, manufacturing and documentation for Electronic Voltage Regulating Transformers.

2.0	RESPONSIBILITIES

It is not the intent to specify herein all the details of design and construction. It shall be the responsibility of the Seller to ensure that the equipment has been engineered, fabricated and tested in accordance with UST design specifications.

2.1	Seller’s Responsibilities

- The Seller shall have full responsibility for compliance with the requirements of this document.

- The Seller shall design, fabricate and supply the equipment completely assembled, wired, tested and ready for installation in accordance with this document.

- The Seller shall be responsible for providing documents and drawings as required by this document.

2.2	Buyer’s Responsibilities

- Receiving and installing the unit (EVR).

- Providing source voltage (input to EVR) within IEEE-519 voltage limits.

- Provide proper clearances around EVR as dictated by UST installation documentation.

3.0	TECHNICAL REQUIREMENTS

3.1	Functional Requirements

The functionality and performance of the equipment shall be as follows:

| 3.1.1 | Unit Rating: | The units shall have a continuous rating of “ XXX” kVA |
| --- | --- | --- |
| 3.1.2 | Phase and Frequency: | The unit shall be 3 phase or single phase, and 60 Hz or 50Hz depending on requirement. |
| 3.1.3 | Input Voltage: | The nominal input voltage shall be “xxx” V +10% to -25% |
| 3.1.4 | Output Voltage: | The nominal output voltage shall be “xxx” V ±3% |
| 3.1.5 | Output Voltage Regulation: | The unit shall regulate each phase independently |
| 3.1.6 | Voltage Regulation Duration: | The unit shall be capable of continuous voltage regulation sampling the incoming voltage level continuously |
| 3.1.7 | Voltage Regulation Variation: | Output voltage regulation shall be constant from 0 to 100% load and for any load power factor |
| 3.1.8 | Response Time | Response time shall be 1 cycle typical; 1.5 cycle maximum regardless of load or load power factor |
| 3.1.9 | Tap Switching Transients: | The unit shall not interrupt the load current when switching taps |
| 3.1.10 | Harmonic Distortion: | The unit shall add no harmonic distortion to the output voltage waveform for any load, load power factor or for linear or non-linear loads |
| 3.1.11 | Surge Suppression: | Surge suppression shall be incorporated with the unit and shall be in accordance with ANSI/IEEE standard C62.41 |
| 3.1.12 | Overload Capacity: | The overload capacity of the unit shall be at least 6,000% for one cycle; 1,000% for one second; 500% for five seconds; 200% for one minute |
| 3.1.13 | Fault Clearing: | The unit shall provide a minimum 1000% fault clearing capacity to permit downstream and load protective devices to operate properly |
| 3.1.14 | Minimum Load | There shall be no minimum or other limitations on load (other than full load and overload) |
| 3.1.15 | Load Power Factor Limitation: | There shall be no minimum or other limitations on load power factor |
| 3.1.16 | Load compatibility: | The unit shall be compatible with all load types without limiting or restricting unit rating or performance |
| 3.1.17 | Current Zero Crossing Sensitivity: | Initiation of tap switching shall be independent of the load current zero crossing |
| 3.1.18 | Efficiency | Efficiency of the unit shall be 97% or higher down to 15% of full load |
| 3.1.19 | Internal Bypass: | The unit shall have an internal automatic electronic bypass that actuates automatically on malfunction or component failure and maintains load current while protecting the unit. Unit shall not require de-energizing to actuate the internal bypass and shall be capable of operation on internal bypass indefinitely. All unit functionality, except voltage regulation, shall be operable while the internal bypass is active |
| 3.1.20 | Noise Attenuation | The unit shall provide noise attenuation of at least 150 dB at 100 kHz common mode; 65 dB at 100 kHz normal mode |
| 3.1.21 | Operating Frequency: | ±3% of nominal frequency |
| 3.1.22 | Audible Noise: | Audible noise of the unit shall be less than 65 dBA at one meter |

3.2	Physical Requirements

Construction and features of the equipment shall be as follows:

| 3.2.1 | Technology: | The unit shall be of the microprocessor-controlled, tap switching, series transformer design type |
| --- | --- | --- |
| 3.2.2 | Switching Semiconductors: | Switches controlling the taps (semiconductors or otherwise) shall not be required to carry full unit current or overload or fault current; full power semiconductors are not permitted |
| 3.2.3 | Transformer: | The unit shall incorporate a shielded isolation transformer (delta-wye), copper-wound, dry type, per ANSI specifications with a typical impedance between 3 to 3.5%. Transformer insulation shall be designed for a maximum temperature rise of 150 C. For units larger than 500kVA the transformer shall be a dry-type, auto-transformer, copper wound, 3-PH (wye-wye). |
| 3.2.4 | Input Connection: | The input shall be a 3 phase delta (3W+G) hardwired to the input circuit breaker included with the unit or for auto-transformer designs the input shall be a 3 phase wye (3W+N+G). |
| 3.2.5 | Output Connection: | The output shall be a 3 phase wye (3W+N+G) hardwired to lug-type connector(s) |
| 3.2.6 | Neutral: | The unit shall provide connections for a neutral that is newly derived, bonded to enclosure with lug-type connector(s) |
| 3.2.7 | Grounding Connection: | The unit shall have an internal grounding connection as a minimum |
| 3.2.8 | Cable Entry/Exit | The unit shall permit cable entry from the top, bottom or sides |
| 3.2.9 | Cooling: | Standard configuration for normal cooling of the unit transformer, and electrical components shall be by natural convection. |
| 3.2.10 | Input Circuit Breaker: | A molded case input circuit breaker rated no less than 125% of unit full load current shall be included in the unit enclosure. An external handle or pushbuttons shall be provided to open, close and, if necessary, charge the circuit breaker |
| 3.2.11 | Remote Alarm Contacts: | Two sets of remote alarm contacts, rated at 125VAC; 0.6A/110VDC; 0.6A/30VDC; 2A, normally closed shall be provided. The alarm contacts shall indicate the unit has auto-bypassed, loss of voltage regulation or tripping of the input circuit breaker for any reason, no power applied to the unit, the power supply has failed, over-temperature condition. |
| 3.2.12 | Display: | The unit shall include a front mounted LCD 2 line backlit display indicating buck/boost display and unit status. |
| 3.2.13 | Enclosure: | The unit enclosure shall be freestanding, NEMA 1, ANSI 61 grey |

3.3	Environmental Requirements

The equipment shall operate within the following ambient environmental conditions:

| 3.3.1 | Ambient Temperature: | Normal Operating Conditions: The unit shall be capable of continuous operation with an ambient air temperature of 32 to 104°F (0 to 40°C) with a relative humidity of 0-95% non-condensing. |
| --- | --- | --- |
| 3.3.2 | Relative Humidity: | The unit shall be capable of continuous operation with a relative humidity of 0-95% non-condensing. |
| 3.3.3 | Operating Altitude: | The unit shall be capable of continuous operation at full load without de-rating at altitudes from 0 to 10,000 ft (3000m) |

3.4	Installation Requirements

Following are the general requirements for installation:

| 3.4.1 | Assembly: | The unit shall be shipped fully assembled. |
| --- | --- | --- |
| 3.4.2 | Setup: | The unit shall require no setup other than installing the appropriate input, output, neutral and grounding conductors. Installation of the unit shall not require field measurements, adjustment, programming or modification of settings |
| 3.4.3 | Special Tools: | No special tools shall be required for installation or maintenance of the unit |

4.0	DOCUMENTATION REQUIREMENTS

Following are the general requirements for documentation:

| 4.1 | Installation, Operation and Maintenance Manual: | One reproducible hard copy and PDF versions shall be supplied. |
| --- | --- | --- |
| 4.2 | Drawings |  |
| 4.3 | Spare Parts | Available as UST option. Spare parts kit typically includes control board with processor, SCR Assembly, MOV, Snubbers, and fuses where appropriate. |

5.0	WARRANTY

Following are the warranty requirements for the equipment:

| 5.1 | Warranty: | The standard equipment shall be covered by the manufacturer’s standard warranty for eighteen (18) months from the date of shipment or twelve (12) from the date of first operation, whichever occurs first. |
| --- | --- | --- |